# APC Rack SNMP + USB Monitoring Installation & Configuration Manual

For Network Engineers: SMX3000LVNC (Primary) and BVN650M1 (Secondary) via VLAN 99

# Technical Overview

- Objective: Enable SNMP monitoring on the primary UPS (SMX3000LVNC) and USB monitoring on the secondary UPS (BVN650M1) using VLAN 99 management network.

- Estimated Time: 1.5–2.5 hours plus a 15-minute buffer for edge cases (e.g., firmware quirks).

- Risks: SNMP string exposure (mitigated via VLAN 99 firewall and enforcing read-only access); halt procedure if Network Management Card (NMC) is absent.

- Change Log Highlights:

- Updated OIDs to PowerNet-MIB v4.2.1.

- Primary model: SMX3000LVNC (3000VA/2700W).

- Script uses AND-logic, stateful and robust parsing.

- BVN USB monitoring via binary/Podman container.

## Rack Baseline

| UPS | Model | VA/Watt | Battery Health | Runtime | Interface |
| --- | --- | --- | --- | --- | --- |
| Primary | SMX3000LVNC | 3000VA/2700W | 92% | ~16 min @1350W (half-load) | SNMP (NMC) |
| Secondary | BVN650M1 | 650VA/360W | N/A | ~10–15 min @180W | USB (apcupsd) |

Note: SMX runtime assumes 92% battery health (degraded from 18 min spec). Verify via NMC self-test (Menu → Test → Runtime Calibration).

# Technical Specifications & Prerequisites

## SNMP Requirements (Primary SMX3000LVNC)

- Version: SNMPv2c (read-only; enforced by access type).

- Key OIDs (PowerNet-MIB v4.2.1):

- Battery Capacity (%): .1.3.6.1.4.1.318.1.1.1.2.2.1.0

- Output Load (%): .1.3.6.1.4.1.318.1.1.1.4.2.3.0

- Runtime Remaining (min): .1.3.6.1.4.1.318.1.1.1.2.2.3.0 (timeticks/6000)

- Battery Status: .1.3.6.1.4.1.318.1.1.1.2.1.1.0

- Traps: On-battery, low-battery (<20%), replace-battery

Bandwidth: <1 Kbps for polling; <10 Kbps for traps

## USB Monitoring (Secondary BVN650M1)

- Interface: USB (monitored via apcupsd on UDM; SNMP not supported)

- Key Metrics: Battery %, load, runtime (polled via software)

- Alerts: Low battery (<20%), runtime <5 min

## Network & Hardware Settings

- VLAN: 99 (Mgmt; SMX Static IP: 10.99.0.2/28 on port 48 GbE non-PoE; BVN USB direct to UDM)

- UDM Integration: SNMP for SMX; apcupsd for BVN

- Prerequisites:

- Access to SMX NMC UI (via DHCP or scan; admin/physical password required)

- apcupsd v3.14.14+ (manual binary or Podman container on UDM)

- Browser, wget/tar, Podman, USB cable (<15 ft for BVN)

- NMC Firmware: AOS 3.x+ for full SNMPv2c

Considerations: If UDM USB unreachable, fallback to BVN LCD; verify UDM USB compatibility with BVN pre-production (lsusb)

# Installation & Configuration Procedure

## Phase 1: Pre-Migration Preparation (45 min)

- UPS Inventory Audit

- Locate both UPS units in rack; note serial numbers and firmware (LCD: Menu > Status > About); verify model numbers.

- Verify NMC presence on SMX (check rear panel for Ethernet port and LEDs). If absent, halt and order AP9631 NMC.

- Record current IP address (likely DHCP); scan VLAN 99 or connect directly via laptop if needed.

- Document UPS details in a "UPS Hero Sheet" (Google Sheets) using the following template:

UPS IDModelS/NIP/InterfaceMAC/USBVLAN PortCommunity/StringNotes

PrimarySMX3000LVNCABC12310.99.0.200:11..99-48mgmt_ro_202592% batt; ~16 min @1350W

SecondaryBVN650M1DEF456USB to UDMN/AUDM USBapcupsdAux <300W; 10-15 min

- Physical Preparation

- Label cables: SMX Ethernet (blue: "SMX-Mgmt → USW-48"); BVN USB (red: "BVN-Aux → UDM-USB"). Photograph rack for documentation.

- Export SMX NMC configuration (UI: Config > Backup); snapshot BVN LCD.

- Staged Validation Plan

- Validate SMX NMC first, then BVN USB.

- Success criteria: SNMP polling/traps on SMX; USB metrics on BVN (<5s response).

- HALT if NMC is absent or access fails.

## Phase 2: Primary UPS (SMX) SNMP Configuration (30 min)

- Access & Basic Network Setup

- Connect laptop to SMX NMC via Ethernet; identify IP via scan or LCD.

- Access NMC UI: [URL] IP]; login with admin credentials.

- Set static IP (10.99.0.2/28), gateway (10.99.0.1); apply changes and verify connectivity (ping UDM).

- Enable SNMPv2c

- Navigate: Config > Network > SNMPv1/v2c; enable SNMP v1/v2c.

- Set community string ("mgmt_ro_2025"); enforce read-only access.

- Add trap receiver (10.99.0.1:161); enable on-battery, low-battery, and replace-battery traps.

- Apply and reboot NMC.

- Verification

- Run: snmpget -v2c -c mgmt_ro_2025 10.99.0.2 .1.3.6.1.4.1.318.1.1.1.2.2.1.0

- Expected output: SNMPv2-SMI::enterprises.318.1.1.1.2.2.1.0 = INTEGER: 92 (battery %)

- If error: Check firewall/ping or verify OID/MIB version.

## Phase 2B: Secondary UPS (BVN) USB Monitoring (15 min)

### Step 2B.1: UDM Setup (USB Direct, Manual Binary)

- Verify UDM USB compatibility (SSH: lsusb, expect "American Power Conversion").

- Install apcupsd (choose one method)

- Pre-compiled Binary (Recommended):

- Download and extract: wget [URL], tar -xzf apcupsd-3.14.14-arm64.tar.gz

- Copy binaries and config: cp apcupsd-3.14.14/sbin/apcupsd /usr/sbin/, cp apcupsd-3.14.14/etc/apcupsd/apcupsd.conf /etc/apcupsd/

- Set executable: chmod +x /usr/sbin/apcupsd

B. Podman Container (Stable):

Run container: podman run -d --name apcupsd --device=/dev/usb/hiddev0 -v /etc/apcupsd:/etc/apcupsd gersilex/apcupsd:latest

Enable restart on boot: podman generate systemd --new --name apcupsd > /etc/systemd/system/apcupsd.service; systemctl enable apcupsd.service

Alternatively, add to /config/scripts/post-boot.sh: podman start apcupsd

C. External Host (Fallback): Use Raspberry Pi on VLAN 99 (10.99.0.3); script via SSH poll.

Connect BVN USB and confirm detection.

Enable Monitoring

Edit /etc/apcupsd/apcupsd.conf: UPSTYPE usb; DEVICE; ONBATTERYDELAY 6; BATTERYLEVEL 20; KILLDELAY 120 (default values otherwise).

Restart apcupsd: systemctl restart apcupsd (binary) or podman restart (container).

Check status: apcaccess status (shows batt/load/runtime).

Configure UDM notifications (e.g., email on battery capacity <20%).

Verification

Run apcaccess: Expect runtime ~10–15 min @180W.

If USB reach fails, fallback to BVN LCD (Menu > Status).

## Phase 3: UniFi UDM Integration (15 min)

- Enable SNMP on UDM (for SMX)

- Console: Settings > CyberSecure > Traffic Logging > SNMP: Enable v2c; set community "mgmt_ro_2025".

- Note: This enables UDM to respond to SNMP polls and to poll SMX using the configured community string.

- Add Devices & Unified Alerts

- Add SMX device: Devices > SNMP Add: 10.99.0.2.

- Configure alerts:

- Low Battery: OID .1.3.6.1.4.1.318.1.1.1.2.2.1.0 <20%

- Critical Runtime: OID .1.3.6.1.4.1.318.1.1.1.2.2.3.0 <5 min (post-conversion)

- Extend alerts to BVN via apcupsd integration.

- Implement tandem monitoring script (polls every 5 min):

- Save script, set executable, and add to crontab or post-boot scripts as appropriate.

- AND logic ensures both UPS units are critical before shutdown.

## Phase 4: Execution & Testing (30–60 min, Off-Hours)

- Staged Enablement

- Connect SMX to port 48; adopt and test SNMP polling/traps (LCD self-test).

- Connect BVN USB to UDM; verify apcaccess; simulate low-battery (partial discharge, safe).

- Full Validation

- Simulate tandem outage by unplugging AC; monitor runtimes and alerts.

- Trap Validation

- Monitor UDM logs: tail -f /var/log/messages | grep TRAP

- SMX LCD: Menu → Test → Simulate Power Failure (10 sec); verify trap received within 5 sec.

- Cancel test via LCD to restore.

- Baseline with Wireshark on VLAN 99 for SNMP traffic (filter: ip.src==10.99.0.2).

- Rollback (If Needed)

- Revert IPs and disconnect hardware if necessary.

- Restore NMC backup; stop apcupsd; document configuration changes.

## Testing & Validation Checklist

- SMX SNMP: OID poll <5s; traps appear in Insights.

- BVN USB: apcaccess reports runtime ~10–15 min; alerts trigger.

- Tandem Script: Triggers warning if both runtimes <3 min; logs status variations.

- VLAN 99: SMX is pingable; BVN detected via USB.

- Runtime: SMX ~16 min @1350W; BVN ~10–15 min @180W.

- Alerts: <20% battery triggers consolidated notifications.

## Troubleshooting

- SMX NMC Fail: Scan IP (DHCP?); reset; collect S/N, firmware, event log, network backup before escalation; verify with ping/snmpwalk.

- BVN USB Silent: Check with lsusb; adjust configuration; fallback to LCD if unreachable.

- OID Errors: Confirm MIB version; use snmpwalk; escalate to Ubiquiti if UDM poll fails.

- Script Glitch: Check logs (/var/log/apcupsd, syslog); verify timeticks; escalate cron issues to UDM forum.

- No NMC: Order AP9631; use LCD interim; escalate procurement if needed.

## Known Limitations

- BVN lacks SNMP: USB polling ~10s latency vs. SMX real-time; LCD fallback available.

- SNMPv2c Security: Enforced RO via access type; VLAN 99 blocks external access—use ACLs for scaling.

- Script Polling: 5-min interval; suitable for rack-level monitoring.

## Post-Migration Optimization (Week 1)

- Consolidate alerts on UDM dashboard; test notification chain (email/Slack).

- Quarterly battery self-tests (LCD); replace if <80% health (SMX RBC132, BVN APCRBC124).

- Security: Rotate SNMP community strings annually; audit VLAN ACLs.

- Expansion: Port 46 available; consider SNMP-enabled PDUs if rack grows.